TRIUN CONSTRUCTION & ENGINEERING Exterior Window Perimeter Sealant Product Selection & Submittal Reference

| PROJECT | Home2 Suites by Hilton — Eagle Pass, TX | PROJECT CODE | H2SEP |
| --- | --- | --- | --- |
| SPEC SECTION | 07 92 00 — Joint Sealants (coordinate w/ 08 51 13) | DATE | August 13, 2026 |
| BASIS OF DESIGN | Quaker Windows & Doors — Installation Guidelines for Quaker Aluminum Products, New Construction Nail Fin Installation with a Drainable Weather Resistant Barrier; QWP part # IG-001, Rev. v1.8, dated 08/04/2023 |  |  |
| PREPARED BY | Triun Construction & Engineering — Project Management |  |  |

# 1.  Governing Requirement

The window manufacturer's installation guide establishes the sealant requirement. Two provisions on page 2 of IG-001 v1.8 control:

IG-001 v1.8, Page 2 — "Sealing" “Quaker recommends 100% silicone (ASTM C920 compliant) neutral cure only sealant. Always clean all areas where sealant will be applied. Failure to do so could result in product or property damage.”

IG-001 v1.8, Page 2 — "Installation" “Nailing flanges and drip caps (integral or applied) do not take the place of window flashing. All windows and doors must be properly flashed and sealed with material compatible sealant for protection against water and air infiltration around the entire perimeter.”

## Requirement summary

| COMPOSITION 100% Silicone | CURE TYPE Neutral Cure Only | STANDARD ASTM C920 | COMPATIBILITY Field-Verified |
| --- | --- | --- | --- |

# 2.  Related Material Standards in the Same Guide

IG-001 sets separate standards for the adjacent materials. These are frequently conflated on submittals — they are distinct requirements and each needs its own product data.

| Material | Requirement per IG-001 v1.8 | Reference |
| --- | --- | --- |
| Perimeter sealant | 100% silicone, neutral cure, ASTM C920 compliant | p. 2 — Sealing |
| Minimally expanding foam | Compliant with AAMA 812-19 | p. 2 — Sealing |
| Self-adhered flashing tape | Meets ASTM D779 performance requirements | p. 2 — Sealing |
| Backer rod | Closed-cell foam backer rod (listed required material) | p. 1 — Materials |
| Surface cleaner | IPA (isopropyl) alcohol (listed required material) | p. 1 — Materials |
| Fasteners | 1½" min. embedment into structural framing; min. 3 full threads, 5/16" head | p. 1 — Fastening |

# 3.  Two Distinct Sealant Duties

IG-001 calls for sealant in ten separate operations, and those operations do not all bond to the same substrates. Splitting them correctly is what determines whether one product or two is required.

| Duty | Where it occurs (IG-001 step) | Must bond to | Controlling property |
| --- | --- | --- | --- |
| DUTY A Concealed | Step 11 bead behind the nail fin at jambs & head; Step 27 mulled-unit fin gaps; Steps 28–29 flashing tape corners and tape-to-frame bead | Housewrap / WRB, sheathing, self-adhered flashing tape, nail fin | Adhesion to low-surface-energy WRB. Low movement. Color irrelevant — fully concealed. |
| DUTY B Exposed | Steps 20, 21, 24, 25 head & sill flashing cap beads and end seals; Step 32 interior bead; frame-to-finish perimeter joint (by others) | Aluminum window frame, head/sill flashing, stucco / EIFS / masonry finish | Color match, UV durability, non-staining on porous finishes, higher ASTM C920 movement class. |

Why this matters Most architectural weatherproofing silicones will not bond to spun-bonded polyolefin housewrap. A single Class 50 weatherseal selected only for the exposed joints will very likely fail the Step 11 bead behind the nail fin — the joint that keeps bulk water out of the wall. This is the most common failure point on nail fin installations.

# 4.  Sealant Application Locations by Install Step

Per IG-001 v1.8, Steps 11 through 32. Use this list for quantity takeoff and for field QC sign-off.

| Step | Location | Bead / requirement | Duty |
| --- | --- | --- | --- |
| 11 | Jambs & head of rough opening, behind the nail fin | Continuous 3/8" bead, no more than 1/2" from edge of opening; must line up with nail hole slots | A — Concealed |
| 11 | Sill of rough opening | NO sealant, or a non-continuous bead — required to allow drainage | — (none) |
| 20 | Bottom of head flashing to top of window | Caulk the seam | B — Exposed |
| 21 | Both ends of head flashing at window | Backer rod + sealant | B — Exposed |
| 24 | Both ends of sill flashing at window | Backer rod + sealant | B — Exposed |
| 25 | Sill flashing to window | Continuous cap bead | B — Exposed |
| 27 | Mulled units — gaps between nail fins / at window joints | Seal remaining gaps and tool in smooth, both sides | A — Concealed |
| 28 | Top corners of head flashing tape | Sealant at corners | A — Concealed |
| 29 | Mulled units — flashing tape to main frame | Continuous bead, tooled smooth; verify no gaps remain | A — Concealed |
| 32 | Interior — entire bottom and up 6" both jambs | Continuous cap bead | B — Interior |

Critical — do not seal the sill Step 11 requires NO sealant at the bottom of the opening, or a non-continuous bead, to allow drainage. A continuous bead at the sill traps water in the opening and defeats the drainable WRB assembly. Confirm this in the field before the units are set.

# 5.  Qualified Products

All products listed are 100% silicone, neutral cure, and ASTM C920 compliant, and therefore satisfy the IG-001 v1.8 requirement on their face. Classifications below are taken from each manufacturer's current published technical data sheet.

| Product | ASTM C920 classification | Movement | Duty | Notes |
| --- | --- | --- | --- | --- |
| DOWSIL 758 Silicone Weather Barrier | Type S, Grade NS, Class 25 | ±25% | A | Purpose-built for this duty. Primerless adhesion to polyethylene-film WRBs, spun-bonded polyolefin and woven air barriers, peel-and-stick WRBs, anodized aluminum, vinyl, PVC, powder coat and Kynar. Peel strength >40 pli unprimed to anodized and powder-coated aluminum. |
| DOWSIL 791 Silicone Weatherproofing | Type S, Grade NS, Class 50, Use NT, M, G, A | ±50% | B | Medium modulus. 7 stock colors plus custom match to virtually any substrate. |
| DOWSIL 795 Silicone Building Sealant | Type S, Grade NS, Class 50 | ±50% | B | Commercial workhorse; weatherseal and structural. Very broad distribution. |
| Sikasil WS-295 | Type S, Grade NS, Class 50, Use NT, M, G, A, O | ±50% | B | Data sheet expressly lists “perimeter weathersealing of doors, windows.” Non-staining; full Use designation list. |
| Tremco Spectrem 2 | Type S, Grade NS, Class 50, Use NT, M, G, A, O | ±50% | B | Expressly listed for perimeter caulking and weatherproofing. Adheres to glass, aluminum, painted metal, stone, concrete, brick, plastics. |
| Tremco Spectrem 1 | Type S, Grade NS, Class 100/50, Use NT, M, G, A, O | +100 / −50% | B | Ultra-low modulus. Lists window perimeters and air barrier transitions. Meets EIMA 300.01 (EIFS); GREENGUARD Gold certified. |
| GE / Momentive SilPruf SCS2000 | Type S, Grade NS, Class 25, Use NT, G, A, O | — | B | Medium modulus, widely stocked; primerless adhesion to most substrates including coated and anodized aluminum. |
| GE / Momentive SilPruf NB SCS9000 | Type S, Grade NS, Class 50, Use A, G, M, O | ±50% | B | Non-bleed, non-staining; formulated to reduce dirt pickup and surface streaking. Use where the finish is porous or stain-sensitive. |
| Pecora 895NST | Class 50, Type S, Grade NS, Use G, A, M, O | ±50% | B | Non-staining (passes ASTM C1248 on marble/granite). Structural and weatherproofing. See Limitation 3 regarding the Use list. |
| Pecora 890NST | Class 100, Type S, Grade NS, Use G, A, M, O | +100 / −50% | B | Ultra-low modulus, non-staining; specifically suited to EIFS. Application temp −20 to 120°F. See Limitation 3. |

# 6.  Recommended Package

## Option 1 — Two-product package (recommended)

RECOMMENDED Duty A — Concealed: DOWSIL 758 Silicone Weather Barrier Sealant. Its published substrate list — polyethylene-film WRBs, spun-bonded polyolefin and woven air barriers, peel-and-stick WRBs, anodized aluminum, vinyl, PVC, powder coat and Kynar — is precisely the substrate list in IG-001 Steps 11 and 28–29. Duty B — Exposed: Sikasil WS-295 or Tremco Spectrem 2. Both are Class 50 with the complete Use NT, M, G, A, O designation, both are non-staining, and both offer a wide stock color range plus custom match.

## Option 2 — Single product for all beads

If a single SKU on site is preferred for field simplicity, use Sikasil WS-295 or Tremco Spectrem 2 throughout — but only after the manufacturer confirms adhesion to the specific WRB and flashing tape in writing. Do not assume it.

## If the exterior finish is EIFS or stucco

Substitute the Duty B product with Tremco Spectrem 1 or Pecora 890NST. Both are ultra-low modulus Class 100 and both are formulated for EIFS; Spectrem 1 additionally meets EIMA Test Method 300.01.

# 7.  Limitations & Exceptions

Limitation 1 — DOWSIL 758 is a concealed-joint product 758 is available in white only, and Dow's data sheet states it is not to be used as an aesthetic weatherseal, nor in structural, below-grade, or continuous water immersion applications. It must not end up on the exposed head and sill flashing cap beads (Steps 20, 21, 24, 25) or the Step 32 interior bead.

Limitation 2 — DOWSIL 758 is Class 25, not Class 50 If the architect's Section 07 92 00 requires Class 50 minimum, 758 does not satisfy that on its face. It remains appropriate for the concealed duty, but the submittal must state the two-product split explicitly so the reviewer does not reject the package on a class mismatch.

Limitation 3 — Pecora Use designations omit “NT” Pecora's published Use list for both 895NST and 890NST is G, A, M, O. Every other product in Section 5 carries NT (non-traffic). If the project specification requires Use NT, confirm with Pecora in writing before submitting — do not assume the omission is a typographical one.

Limitation 4 — IG-001 does not specify a C920 class ASTM C920 requires a Type (S/M), Grade (NS/P), Class (12½, 25, 35, 50, 100/50) and Use designations. Quaker states only “ASTM C920 compliant.” For an exterior perimeter joint, Type S, Grade NS, Class 25 minimum, Use NT, G, A, O would be the expected call. If Section 07 92 00 is likewise silent, issue an RFI to the architect rather than selecting the class unilaterally.

# 8.  Pre-Order Action Items

- Obtain the WRB and flashing tape manufacturers and product names actually being installed, and submit them to the sealant manufacturer for ASTM C794 adhesion and ASTM C1087 compatibility testing. All manufacturers listed in Section 5 perform this at no cost on submitted substrates. This is the single highest-value step in the package.

- Confirm the exterior finish assembly (stucco, EIFS, brick, metal panel). This determines whether a non-staining grade per ASTM C1248 is required and whether an ultra-low modulus Class 100 product is warranted.

- Confirm the required ASTM C920 class in Section 07 92 00. If the specification is silent, issue an RFI per Limitation 4 before ordering.

- Order color to match the window frame finish, and confirm custom-match lead time. Custom color is typically 2–4 weeks and is a recurring closeout delay if left to the end.

- Plan for Eagle Pass heat. Silicone skins in roughly 15 minutes at 77°F and materially faster in summer conditions, and IG-001 requires tooling before skin-over at several steps. Sequence short bead runs and keep the IPA wipe — also required by IG-001 — ahead of the gun.

- Verify backer rod is closed-cell foam and sized to compress approximately 25% in the joint, per the sealant manufacturer's joint design guidance.

# 9.  Excluded Materials

Not permitted under IG-001 v1.8 The requirement for “100% silicone … neutral cure only” excludes each of the following, regardless of any other performance claim: Acetoxy-cure (acid-cure) silicone — can attack anodized and painted aluminum finishes and is incompatible with many WRB and self-adhered flashing adhesives. Polyurethane and hybrid / SMP sealants — not 100% silicone. Acrylic latex and siliconized acrylic caulk — not 100% silicone; inadequate movement capability and UV durability for this application.

# 10.  References

- Quaker Windows & Doors — Installation Guidelines, QWP part # IG-001 v1.8, dated 08/04/2023 (pages 1, 2, and Steps 11–32).

- ASTM C920 — Standard Specification for Elastomeric Joint Sealants.

- ASTM C719 — Adhesion and Cohesion of Elastomeric Joint Sealants Under Cyclic Movement (Hockman Cycle).

- ASTM C794 — Adhesion-in-Peel of Elastomeric Joint Sealants.

- ASTM C1248 — Staining of Porous Substrate by Joint Sealants.

- ASTM D779 — flashing tape performance (per IG-001 p. 2); AAMA 812-19 — minimally expanding foam (per IG-001 p. 2).

- Manufacturer technical data sheets: Dow (DOWSIL 758, 791, 795); Sika (Sikasil WS-295); Tremco (Spectrem 1, Spectrem 2); Momentive / GE Silicones (SilPruf SCS2000, SilPruf NB SCS9000); Pecora (895NST, 890NST).

Note: Quaker's language is “recommends.” Where the project specification, the architect's Section 07 92 00, or an approved submittal imposes a stricter requirement, that requirement governs. Product classifications above are transcribed from manufacturer data sheets current as of the date of this document and should be re-verified against the data sheet submitted with the product.